## Amendments
Amendment | WIMES | Specification Reference | Original Clause Wording (If Applicable) | Amended Clause Wording or Amendment Details (refer also to relevant worksheets for yellow highlighted cells) | Date Ratified | 1.01
2023
1/23 | 8.08 | Table 1 - gasket selection and associated guidance notes | N/A - refer to Table 1. | Tables 1, 2 and 3 in the Guidance Notes deleted. In the 'Tightening Torque' column in Table 1, references to Tables 1, 2 and 3 replaced with a reference to a new note 5, reading as follows: "The tightening torque shall be selected in consultation with the gasket and pipework manufacturer. The objective is to achieve a suitable bolt pre-load which will ensure the joint is effectively sealed without overstressing the gasket, bolts and flange materials". | 2023-06-21 | 1.02
2/23 | 3.02 | Clause 6.4.7.1, Tray, 2 | "Tray may be made of mild steel (hot dip galvanised after manufacture in accordance with BS EN ISO 1461), stainless steel, GRP or U-PVC." | "Tray may be made of mild steel (hot dip galvanised after manufacture in accordance with BS EN ISO 1461), Magnelis ZM310 coated mild steel, stainless steel, GRP or U-PVC." | 2023-09-14 | 1.03
3/23 | 3.02 | Clause 6.4.3.2b) | "The type of sealing systems used shall be approved by the Purchaser and shall be selected and installed with due regard to environmental and hazardous area requirements (refer to WIMES 3.02(D)). The type of sealing systems used shall be selected from the following options: a) Approved water, gas and fire sealing transit units with fillers and insert blocks fitted to suit all cables and conduits; b) Approved fire retardant and gas and watertight sealing system, comprising insert sleeves to ensure cable separation and a silicone-based sealant; c) Approved fire retardant and gas and watertight sealing system, comprising an expanding, two-component polyurethane resin formulation, which cures into a high density, hydrolysis resistant compound; or d) Approved gas and watertight sealing system, comprising flexible, interlocking foam inserts, to ensure cable separation and a silicone-based sealant." | "The type of sealing systems used shall be approved by the Purchaser and shall be selected and installed with due regard to environmental and hazardous area requirements (refer to WIMES 3.02(D)). The type of sealing systems used shall be selected from the following options: a) Approved water, gas and fire sealing transit units with fillers and insert blocks fitted to suit all cables and conduits; b) Approved fire retardant (if required) and gas and watertight sealing system, comprising insert sleeves to ensure cable separation and a silicone-based sealant; c) Approved fire retardant and gas and watertight sealing system, comprising an expanding, two-component polyurethane resin formulation, which cures into a high density, hydrolysis resistant compound; or d) Approved gas and watertight sealing system, comprising flexible, interlocking foam inserts, to ensure cable separation and a silicone-based sealant." | 2023-09-14 | 1.04
4/23 | 3.02 | 6.5.1.1.5 | "Cable glands shall be provided with shrouds to minimise the risk of dirt or foreign substances gathering on the cable gland body and/or cable to cable gland interface. Where possible, the shroud colour shall match the cable sheath colour (refer to Guidance Notes)." | Clause deleted. | 2023-09-14 | 1.05
5/23 | 3.02(D) | Section 4.0 | N/A - new clause added. | "Shrouds shall not be fitted cable glands to ensure that visual inspection of the installation can be undertaken without having to move the shroud and possibly damage or compromise the installation." | 2023-09-14 | 1.07
6/23 | 8.02(B) | Appendix A | N/A - refer to Appendix A | EPDM option deleted for: a) Filling line and associated valves (as a liner for steel components) b) Diaphragm pump seals c) Peristaltic pump hoses d) Gaskets and o-rings | 2023-12-06 | 1.08
2024
1/24 | 8.08 | Appendix C 3.4 - SS03 (thin-walled pipework) - Note 1 | "SS 03 shall only be used where there is no potential for pressures to be below atmospheric, severe temperature cycling or vibration." | "The following requirements shall apply to the use/design of SS03, as a minimum: a) It shall not be used for applications where sub-atmospheric pressures are expected. Unless otherwise approved by the Purchaser, it shall not be used for long lengths of pipework connecting different items of plant or processes, unless a surge analysis has been performed to verify that sub-atmospheric pressures will not occur within the pipework. b) It shall not be used for applications where the process liquid will contain significant levels of grit or sand e.g. grit transfer pipework, pipework upstream of grit removal processes, raw water pumping station inlet pipework, etc, noting that its reduced wall thickness will make it more susceptible to failure via erosion and/or corrosion, due to continuous removal of the passivating layer. c) It shall not be used for pipework incorporating chemical dosing points, upstream of the point at which the chemical is assumed to be completely mixed with the process fluid, noting that its reduced wall thickness will make it more susceptible to failure via general and/or localised ‘pin hole’ corrosion. d) If it will be used for applications where the process liquid will contain high chloride levels, selection of the 304/304L grade shall only be permitted if it can be verified by sampling that the chloride levels in the liquid are less than 200 ppm, noting that its reduced wall thickness will make the 304/304L grade more susceptible to failure via pitting corrosion. e) It shall not be used for applications where the process liquid velocity during normal operation will exceed 1.4 m/s, noting that its reduced wall thickness will make it more susceptible to failure via surge at liquid velocities above this value. f) Unless otherwise approved by the Purchaser, it shall not be used for applications where the process liquid temperature will exceed 60°C, noting that its reduced wall thickness will make it more susceptible to failure via thermally induced fatigue. g) Special attention shall be paid to its support and restraint, and to the support and restraint of connected fittings and equipment (e.g. test/sampling points and pump and valves, etc), noting that its reduced wall thickness will make it more susceptible to failure via: i) Buckling and plastic deformation; and ii) Vibration-induced fatigue. For the same reason outlined in item i) above, special care shall also be taken to avoid accidental damage due to careless mechanical handling during its delivery and installation/erection. h) It shall be supported by elastomer lined pipe clamps, saddles or any other supports which do not exert significant point loadings on the pipe surface. U-bolt type clamps shall not be used due to the increased likelihood of these clamps deforming or damaging its surface (refer also to clause 6.7.1.8 of WIMES 8.08). i) The pipework design shall be verified to comply with established standards, such as BS EN 13480-3, either by calculation or by comparative studies with existing pipework assemblies operating under similar conditions (refer to Appendix A3.1 of BS EN 13480-3 for the definition of comparative studies) unless: i) It is similar in all respects to thin-wall stainless steel pipework systems already in use by the Purchaser or other water companies (references shall be provided); and/or ii) It comprises standard, catalogue-sourced pipes and fittings (e.g. bends/elbows, tees, reducers, end-caps, etc.). j) Unless otherwise approved by the Purchaser, it shall not be used for pipework sizes above DN 700, noting that its reduced wall thickness makes it more susceptible to failure by buckling and deformation." | 2024-04-16 | 1.09
2/24 | 8.08 | Table D1 - Pipework selection guide for liquids and accompanying notes | N/A - refer to table D1. | Refer to 'WIMES 8.08 - Table D1' worksheet | 2024-04-16 | 1.10
3/24 | 8.02(B) | Clause 6.5.3.1.2 | "The calibration vessel venting location shall be as specified/stated on the DATA SHEET." | "If approved by the Purchaser, a calibration vessel shall not be provided, if the dosing pumps can display the dosing chemical flow rate and are capable of degassing the pipework. If a calibration vessel is provided, the venting location shall be as specified/stated on the DATA SHEET." | 2023-12-06 | 1.11
4/24 | 8.02(B) | Section 6.5.3.3, General | N/A - new content added. | New clause 2 added: "At dosing chemical flow rates less than 10 l/hr, 6 mm OD (4 mm ID) flexible tubing shall be used instead of rigid pipework to ensure that the fluid velocity is high enough to flush out any gas bubbles formed and avoid gas-locking in elbows, etc.” | 2023-12-06 | 1.12
5/24 | 8.02(I) | Clause 6.5.3.1.2 | "The calibration vessel venting location shall be as specified/stated on the DATA SHEET." | "If approved by the Purchaser, a calibration vessel shall not be provided, if the dosing pumps can display the dosing chemical flow rate and are capable of degassing the pipework. If a calibration vessel is provided, the venting location shall be as specified/stated on the DATA SHEET." | 2023-12-06 | 1.14
6/24 | 8.02(I) | Section 6.5.3.3, General | N/A - new content added. | New clause 2 added: "At dosing chemical flow rates less than 10 l/hr, 6 mm OD (4 mm ID) flexible tubing shall be used instead of rigid pipework to ensure that the fluid velocity is high enough to flush out any gas bubbles formed and avoid gas-locking in elbows, etc.” | 2023-12-06 | 1.15
7/24 | 8.09 | AppendIx K | N/A - new content added. | New note added: "Ball valves sized less than DN 80 are acceptable for use with any fluid if the valve will be used for draining/bleeding, flushing, sampling or testing, etc. of pipework". | 2023-12-06 | 1.16
8/24 | 8.02 (General) | Clause 6.1.12.2.1 | "Unless otherwise approved by the Purchaser, the Equipment shall be provided with mains-supplied wholesome water fed emergency washing facilities, comprising showers and eye washes." | "Unless otherwise approved by the Purchaser, the Equipment shall be provided with direct mains-supplied wholesome water fed emergency washing facilities, comprising showers and eye washes. The supply of water to emergency washing facilities from an onsite booster pump shall only be allowed if: a) Suitable backflow prevention measures are taken to prevent contamination of the water supply to the emergency washing facilities in compliance with the Water Supply (Water Fittings) Regulations, byelaws (e.g. an air or tap gap arrangement or a mechanical backflow prevention device); and b) Suitable measures are taken to mitigate the risk the emergency washing facilities being unavailable or not working effectively due to booster set failure or demand for water supplies from other onsite processes." | 2024-02-15 | 1.17
9/24 | 8.02(B) | Clause 6.5.3.1.4 | #VALUE! | #VALUE! | 2024-06-04 | 1.18
10/24 | 8.02(D) | Appendix A | #VALUE! | Add HDPE as an additional filling line material, subject to approval by the Purchaser. | 2024-06-04 | 1.19
11/24 | 8.09 | Appendix K | N/A - refer to Appendix K | Appendix K amended to allow resilient seated, concentric butterfly valves to be used with air, up to the maximum working temperature of the elastomeric seating material (refer to cell Y14 of 'WIMES 8.09 - Appendix K (1)' worksheet). | 2024-06-04 | 2.01
12/24 | 8.02 (General) | 6.3.2.2, General, 12d) | 12. Each tank shall be provided with a label(s), detailing the following information: a) The name of the stored chemical; b) The concentration of the stored chemical; c) Relevant COSHH data; d) The maximum fill capacity; and e) The contact number in the event of an emergency/spill. | Amended to - "d) The tank working (i.e. useable) capacity (refer to clause 6.3.2.2, General, 9)" | 2024-06-04 | 2.02
13/24 | 8.08 | Clause 10.2.2.13 | Refer to Figure 1 - Methodology for Calculating System Test Pressure | Figure 1 amended to included revised definitions of CSP and MDPc (refer to 'WIMES 8.08 - Figure 1 worksheet). | 2024-06-04 | 2.03
14/24 | 9.02 | Clause 6.7.4.3 | The type of fixing required for securing flooring panels to steelwork shall be as specified on the DATA SHEET. Examples of approved fixings are shown in Figure 11. | New sentence 3 added - "The clips shall be coloured yellow to aid identification for inspection purposes." | 2024-07-09 | 2.04
2025
1/25 | 9.02 | Clause 3.0.1 | The operating environment of the PAF (i.e. the site location, corrosivity category, hazardous area classification, etc.) shall be as specified on the DATA SHEET. | New sentence 2 added - 'The corrosivity category and the corresponding corrosion protection/prevention measures shall comply with Table 5 of Wimes 8.03.’ | 2024-12-04 | 3.01
2/25 | 8.08 | Clause 6.11.2b) | Pipework that will be used to convey sludge (>1.5 % DS), scum, grit, Fats Oils & Greases (FOG) or liquids containing solids that will settle-out at low fluid velocities and that cannot be sized such that the minimum flow velocities specified in clause 6.10.1.1 can be maintained, shall be designed and installed in accordance with the following requirements, as a minimum: a) It shall incorporate rodding or jetting points (minimum size DN 50), spaced at maximum intervals of 100 m, with suitable access and drain points to allow effective cleaning of the pipework. Rodding/jetting points shall enter the pipe at an angle suitable to direct the rodding/jetting in the direction of flow; b) It shall incorporate long radius bends; c) It shall have a minimum size of DN 80; d) Taper reducers shall be of the flat top, eccentric type; e) High points and inverted ‘U’ sections shall be avoided, unless inverted U sections are essential to prevent dry running or siphonic flows; and f) If specified in the PARTICULAR SPECIFICATION, FOG pipework shall be installed so that pigging systems can be retrofitted without taking the pipework out of service. | Amended to - "b) It shall incorporate long radius bends (not applicable to sludges that have DS contents less than that of primary sludge e.g. humus sludge, RAS, SAS)"; | 2025-01-06 | 3.02
3/25 | 9.02 | Clause 6.8.3.2.2 | The clear space between the hand-rail and the knee-rail and between the knee-rail and the top of the toe plate, shall not exceed 500 mm (BS EN ISO 14122-3, clause 7.1.4). | Amended to - "The clear space between the hand-rail and the knee-rail and between the knee-rail and the top of the toe plate, shall not exceed 470 mm (clause 3(c), Schedule 2 of the Working at Height Regulations 2005). | 2024-12-04 | 3.02(B)
4/25 | 8.08 | Table 1 - gasket selection and associated guidance notes | N/A - refer to Table 1. | In column 1, the ‘Hot water (CHP/THP)’ category amended to 'Hot water/hot sludge (CHP/THP)'. In the 'Hot water/hot sludge (CHP/THP)' category, the choice of gasket material(s) amended to 'AF + NBR binder or expanded PTFE'. | 2024-12-18
5/25 | 3.06 | Clause 6.14.8 | The circuit breaker shall trip in the event of any of the following: a) Overload; b) Short-circuit; c) Earth-fault (restricted protection); and/or d) Earth leakage fault (restricted protection). | The circuit breaker shall trip in the event of any of the following: a) Overload; b) Short-circuit; c) Earth fault; and/or d) Restricted earth fault (optional based on the cable length between the CB and the alternator). All protection functions shall have readily adjustable current and time settings. | 2024-12-10 | 3.02(C)
6/25 | 8.08 | Clause 6.1.9 | Pipework is deemed to be exempt from the Pressure Equipment (Safety) Regulations, unless it will convey any of the following: a) Steam; b) Air at pressures above 0.5 barg; or c) Fluids, which may be mixtures of liquids, gases and vapours, where the gas or vapour phase may exert a pressure in excess of 0.5 bar above atmospheric pressure: Guidance Note - According to paragraph 1b) of Schedule 1 of the Pressure Equipment Safety Regulations (PESR) and associated guidance, pipework comprising “networks for the supply, distribution and discharge of water and associated equipment” (where water is intended to include potable water, waste water and effluent, and sewage) is excluded from the requirements of the Pressure Equipment Regulations. | Pipework comprising "networks for the supply, distribution and discharge of water" (where water is deemed to include potable water, waste water and effluent, and sewage) is excluded from the scope of the Pressure Equipment (Safety) Regulations (refer to Schedule 1 paragraph 1(b)). | 2025-03-27 | 3.02(D)
7/25 | 8.08 | Clause 6.8.1.5.3 | Purging, flushing and draining points shall be sized at 25 % of the parent pipe size, subject to: a) A minimum size of DN 25 for pipework conveying water and screened waste water, and b) A minimum size of DN 80, for pipework conveying unscreened waste water and sludge. | Purging, flushing and draining points shall be sized to allow pipework to be purged/flushed/drained within a reasonable time, subject to: a) A minimum size of DN 25 for pipework conveying water and screened waste water, and b) A minimum size of DN 80, for pipework conveying unscreened waste water and sludge. | 2025-06-25 | 3.02(E)
8/25 | 8.08 | Clause 10.2.1.2c) | Pressure testing shall comply with the following, as a minimum: a) The HSE Safety requirements for pressure testing - Guidance Note GS4; b) The Pressure Systems Safety Regulations and ACOP L122; c) Water Industry Guidance Note 4-01-03 - Guide To Pressure Testing Of Pressure Pipes And Fittings For Use By Public Water Suppliers; and d) Any pressure testing guidelines issued by the Purchaser. | Pressure testing shall comply with the following, as a minimum: a) The HSE Safety requirements for pressure testing - Guidance Note GS4; b) The Pressure Systems Safety Regulations and ACOP L122; c) Water Industry Specification (WIS) 4-01-03 - Specification for hydrostatic pressure testing of polyethylene and polyethylene barrier water supply pipelines and sewer rising mains (if the pipework is made from PE); d) BS EN 805 (if the pipework is made from DI, steel, GRP, PVC-O or any other non-visco elastic material); e) BS EN 13480 and/or ASME B31.3 (if the pipework has been specifically designed in accordance with these standards); and f) Any pressure testing guidelines issued by the Purchaser. | 2025-06-25 | 3.02(F)
9/25 | 8.09 | Clause A1.1.1.6.h) iii) | Specification of the following performance and/or design requirements shall be via the DATA SHEET/SCHEDULE or an alternative means, as defined by the Purchaser: iii) A bypass valve (refer to Guidance Notes) Guidance Note - The main reason to specify a bypass valve is to reduce the differential pressure across the main valve and therefore reduce the operating torque, which can allow more economical gearboxes/actuators to be fitted. Bypass valves also allow delayed downstream filling of pipelines, which can be beneficial for network safety. Bypass valves typically start to become a beneficial option on valves sized above DN 400. | iii) A bypass valve shall (or shall not) be provided for valves greater than 350 mm nominal bore according to the following criteria: DN (mm) x pressure difference (bar) is </= 1000 - no bypass required DN (mm) x pressure difference (bar) is greater than 1000 but less than 3000 - Purchaser to specify requirement based on specific application DN (mm) x pressure difference (bar) is >/= 3000 - bypass required or if required for network safety purposes, as specified on the DATA SHEET. Guidance Note - For metal-seated gate valves, the main reason to specify a bypass valve is to reduce the differential pressure across the main valve and therefore reduce the operating torque, which can allow more economical gearboxes/actuators to be fitted. For resilient-seated gate valves, however, the operating torque is largely independent of the valve differential pressure and the main reason to specify a bypass valve is to prevent waterjet damage of the seat at small valve openings. Bypass valves also allow delayed downstream filling of pipelines, which can be beneficial for network safety/colour issues. Bypass valves typically start to become a beneficial option on valves sized above DN 400. | 2025-07-25 | 3.02(G)
10/25 | 8.05 | Clause 6.2.2.1 | N/A - new content added. | New sub-clause e) added: "Backflow prevention facilities. A documented risk assessment shall be undertaken to determine the appropriate method of backflow prevention considering the hazardous/toxic nature of the scrubbing liquid and the consequences of backflow. | 2025-06-25 | 3.02(H)
11/25 | 8.08 | Section 6.7.1 | N/A - new content added. | New clause added: "Independent supports for valves shall be provided, where any of the following factors could result in excessive stresses in pipework, machinery, components, tanks, etc.: a) The weight of the valve and the distance from its nearest support; b) The pipework material and wall thickness; and/or c) If dismantling the pipework for maintenance (e.g. pump removal) could leave the section incorporating the valve cantilevered". | 2025-06-25 | 3.03
12/25 | 8.02 (General) | Clause 6.1.4.1, Location and Installation, 3 | N/A - new content added. | New sub-clause i) added: "Pipework systems containing different dosing chemicals may be installed in the same duct/trough, subject to the satisfactory outcome of a documented risk assessment. The risk assessment shall consider the likelihood of the pipework system secondary containments failing at the same time (or of a leak from one dosing line affecting the integrity of the secondary containment of the other dosing lines) and the hazardous/toxic properties (or otherwise) of the dosing chemical reaction products." | 2025-07-25
13/25 | 8.08 | Section 7.3 | N/A - new content added. | New clause added (for both inlet and outlet pipework): "If connections for pump draining, venting or priming and/or pump test points, pressure gauges, etc. are not integral to the pump, they shall be incorporated in the adjacent inlet/outlet pipework, as appropriate". | 2025-06-25 | 3.04
2026 | [5 empty] | 3.05
1/26 | 3.01 | Clause 6.3.1.16 (paragraph 1) | The colour of the Assembly shall be as specified on the GENERAL DATA SHEET and be a semi-gloss finish. | The colour of the Assembly shall be light grey (RAL 7035) and the paint shall have a textured finish. | 2025-09-01
2/26 | 8.09 | Appendix K | N/A - refer to Appendix K | Appendix K amended to allow gate valves to be used as ECVs/AECVs for biogas duties, subject to Purchaser approval (refer to cells Q15 and R15 of 'WIMES 8.09 - Appendix K (2)' worksheet). | 2025-12-04
3/26 | 8.08 | Clause 6.9.6.3a) | Couplings shall comply with the following requirements, as a minimum: a) Where they are not of the self-anchoring type, they shall be suitably tied, anchored or guided to resist end forces arising from fluid pressure and/or frictional resistance to pipe movement; With respect to item a), couplings shall be tied to the nearest flange, restraining structure, thrust block or wall, if confimred to be structually suitable. | Couplings shall comply with the following requirements, as a minimum: a) Where they are not of the self-anchoring type, they shall be suitably tied to esnsure that the two connecting sections of pipe cannot separate due to the forces arising from fluid pressure, thermal expansion and/or frictional resistance to pipe movement; With respect to item a), couplings shall have a minimum of 2 tie rods, increasing in number depending on the thruxt forces involved. The use of U bolts/straps or pipe supports is not permitted to restrain the pipework when non-self anchoring flange adaptors or couplings are used. | 2025-12-04
4/26 | 8.08 | Clause 6.8.1.5.3 (as amended by amendment 7/25) | Purging, flushing and draining points shall be sized to allow pipework to be purged/flushed/drained within a reasonable time, subject to: a) A minimum size of DN 25 for pipework conveying water and screened waste water, and b) A minimum size of DN 80, for pipework conveying unscreened waste water and sludge. | Content added to clause: For item b), this minimum size may be reduced to DN 50 on approval e.g. for short lengths of pipework where the reduced size will not significantly affect the purging/flushing/draining time. | 2025-12-04
5/26 | 8.08 | Section 6.4 | N/A - new content added. | New clause added: In addition to being able to withstand the maximum and minimum temperatures imposed on it during normal operating conditions (i.e. due to ambient conditions and the process fluid flowing through it), the pipework shall be designed to withstand the maximum and minimum temperatures imposed on it by ambient conditions when it is empty/out-of-service with lagging removed and trace heating isolated, including freezing conditions and additional sources of heat such as solar gain. | 2025-12-04
6/26 | 1.02 | Clause 7.2.2.2 (Guidance Note) | Where no acceptance grade is specified, a default grade applies, which for the ‘water industry’ is 2B (10 kW < P2 < 100 kW) and 1B (P2 > 100 kW); | #VALUE! | 2025-12-04
7/26 | 8.08 | PE 80 table (page 117) | #VALUE! | #VALUE! | 2025-12-04
8/26 | 8.08 | Section 10.2 (title) | 10.2 Pressure (Strength) Testing | 10.2 Pressure (Leak) Testing | 2025-12-04
9/26 | 8.08 | Clause 10.2.1.2 (as amended by amendment 8/25): | Pressure testing shall comply with the following, as a minimum: a) The HSE Safety requirements for pressure testing - Guidance Note GS4; b) The Pressure Systems Safety Regulations and ACOP L122; c) Water Industry Specification (WIS) 4-01-03 - Specification for hydrostatic pressure testing of polyethylene and polyethylene barrier water supply pipelines and sewer rising mains (if the pipework is made from PE); d) BS EN 805 (if the pipework is made from DI, steel, GRP, PVC-O or any other non-visco elastic material); e) BS EN 13480 and/or ASME B31.3 (if the pipework has been specifically designed in accordance with these standards); and f) Any pressure testing guidelines issued by the Purchaser. | Sub-clause e) deleted. | 2025-12-04
10/26 | 8.08 | Clause 10.2.2.5 | Where the design temperature is above the test temperature, the minimum test pressure shall be calculated in accordance with an approved standard/code (e.g. BS EN 13480 3 or ASME B31.3 for steel pipework). | Clause deleted. | 2025-12-04
11/26 | 8.08 | Clause 6.1.6 | If any of the following criteria apply, the design of steel pipework shall comply with BS EN 13480-3 and/or ASME B31.3: a) The pipework has an MDP of > 16 bar; b) The pipework will convey steam or steam condensate; or c) This specific requirement has been specified in the SHELL or PARTICULAR SPECIFICATION. | If any of the following criteria apply, the design of steel pipework shall comply with BS EN 13480 (all rellevant parts including strength testing) and/or ASME B31.3: a) The pipework has an MDP of > 16 bar; b) The pipework will convey steam or steam condensate; or c) This specific requirement has been specified in the SHELL or PARTICULAR SPECIFICATION. | 2025-12-04 | 5.02
12/26 | 3.04 | Section 6.3.2.4, Cable Management Systems (CMS) | N/A - new content added. | New clause added: To mitigate the likelihood of electromagnetic interference, Band I (extra-low voltage) and Band II (low voltage) cables shall be installed in separate trunking and where practicable, maintain a minimum segregation of 300 mm. | 2026-02-01
13/26 | 5.04 | Sections 2.3 and 5.2.2 | Refer to WIMES 5.04 - Sections 2.3 & 5.2.2 worksheet | Refer to WIMES 5.04 - Sections 2.3 & 5.2.2 worksheet | 2026-04-01 | 5.03
5.04
5.05
6.03
7.01
7.02
7.03
7.04
8.01(A)
8.01(B)
8.02 (General)
8.02(A)
8.02(B)
8.02(C)
8.02(D)
8.02(E)
8.02(F)
8.02(G)
8.02(H)
8.02(I)
8.03
8.04
8.05
8.06
8.07
8.08
8.09
8.10
8.11
8.12
8.13
8.14
8.15
8.16
9.01
9.02

## WIMES 8.08 - Table D1
| Ductile Iron | Carbon steel | Stainless steel | Copper | UPVC | ABS | PE 80 | PE 100 | Polybutylene | Steel wire braid reinforced rubber hose | Notes
WATER TREATMENT APPLICATIONS | [10 empty] | No. | Details
Raw water | DI 01 | CS 01 | SS 01 | 1 | 2, 3, 4 |  | 2, 4 | 2 | 6 |  | 1 | Unsuitable because of the high likelihood of theft, high cost relative to other options and restricted size range
Intermediate and treated water (including potable water) |  |  | SS 01, SS 03 | [7 empty] | 2 | Only use within manufacturer's rated pressure-temperature envelope (refer to specification)
Process waste water/drainage | [10 empty] | 3 | Do not use outdoors unless insulated or wrapped with an opaque material, due to the likelihood of embrittlement by the ultra-violet radiation in sunlight
Sludge (all types) | [6 empty] | 5 |  |  |  | 4 | Do not use where there is a high likelihood of mechanical damage e.g. valve chambers
Washwater (e.g. for filter backwash applications) |  |  | SS 01, SS03, SS 04, SS 05 | CU 01, CU 02 |  |  | 2, 4 |  |  |  | 5 | Not available in suitable sizes
Pump seal flush | 6 |  | SS 04, SS 05 |  |  |  |  | 6 |  |  | 6 | Not designed for this application
Manual sampling |  |  | SS 04, SS 05 | CU 01 | 7 | [5 empty] | 7 | Unsuitable for flaming
Auto-sampling (e.g. on backboards, etc.) |  |  | SS 04, SS 05 | CU 01, CU 02 | 2, 3, 4 |  | 2, 4 |  |  |  | 8 | The erosion/corrosion rate is likely to increase significantly if the lining is worn away
Instrumentation (gauges, transducers, switches) | [10 empty] | 9 | The normally excellent corrosion resistance may be adversely affected by erosion of the passivating layer
Chemical dosing (e.g. disinfection, pH correction, etc.) | Refer to WIMES 8.02 | [9 empty] | 10 | Unsuitable because the pressures in de-watered sludge pumping systems are likely to be above the pipework pressure rating
WASTE WATER TREATMENT APPLICATIONS | [10 empty] | 11 | Only use for short lengths from fixed pipework to skips
Raw sewage | DI 02 | CS 02 | SS01 | 1 | 2, 3, 4 |  | 6 | 2 | 6 | 6 | 12 | Unsuitable because of the high liquid temperature
Intermediate & treated waste water, storm water |  |  | SS 01, SS03 | [7 empty] | 13 | Do not use if H2S is present due to risk of corrosion
Process waste water/drainage | [10 empty] | 14 | Use stainless steel if pipework outdoors or in a high corrosivitiy environment
Grit-laden waste water (specifically associated with grit removal, transfer and treatment equipment) |  | CS 02 (8) | SS 01 (9) | [7 empty] | 15 | Unsuitable because copper accelerates the oxidation rate of petroleum based hydraulic fluids
FOG or scum laden waste water |  | CS 02 | SS 01, SS03 | [7 empty] | 16 | Unsuitable because the pressures in hydraulic systems are likely to be above the pipework pressure rating and/or the high risk of pipework breakage/fluid leakage into process streams
Sludge (primary, humus, SAS and digested) | [10 empty] | 17 | Use stainless steel because it has superior corrosion resistance
Thickened sludge (~7%) | [10 empty] | 18 | Use stainless steel because it has superior mechanical properties
Dewatered sludge (~25%) |  |  | SS01 |  | 10 |  |  | 10 |  | 11 | 19 | Use stainless steel or copper because they have superior corrosion resistance
Hot water and steam condensate (CHP/THP) | 6 | CS 03 | SS02 |  | 12 |  |  |  |  | 6 | 20 | Use U-PVC or PE 100 due to significantly lower cost
Washwater | DI 02 | CS 02, CS 05 | SS 01, SS03, SS 04, SS 05 | CU 01, CU 02 (13) | 2, 3, 4 |  | 2, 4 | 2 |  |  | 21 | Flexible lubrication pipework shall comprise 6 mm OD black nylon tube complying with BS 5409 and shall be suitably rated for the application.
Pump seal flush | 6 |  | SS 04, SS 05 |  |  |  |  | 6 |  |  | 22 | Only use for short lengths (< 2 m)
Instrumentation (gauges, transducers, switches)
Chemical dosing (e.g. P removal, septicity control, etc.) | Refer to WIMES 8.02
FUEL OIL (DIESEL), HYDRAULIC FLUID AND LUBRICANTS
Fuel oil (diesel) | Refer to WIMES 3.06
Hydraulic fluid | 6 | CS 06 (14) | SS 06 | 15 | 16 |  |  |  | 6 | 22
Lubricants (oils and greases) |  | 17 | SS 04 (21) | 18 | [5 empty] | 6
BUILDING SERVICES APPLICATIONS (INDOORS)
Drinking water | 6 | 19 | SS 04, SS 05 | CU 01, CU 02 | [5 empty] | 6
Hot water (for washing and central heating) (up to 90°C) |  |  |  |  | 12
Waste water (from kitchens, toilets, etc.) |  | 20 |  | 6 |  | 20 | 5 |  | 6

## WIMES 8.09 - Appendix K (1)
DUTY |  | ISOLATING | [11 empty] | REGULATING | [10 empty] | CONTROL |  |  | CHECK (NON-RETURN) | [12 empty] | SAFETY |  |  | AIR |  |  |  |  | MISCELL.
VALVE TYPE |  | A 1.1 Wedge gate - cast iron (RS) (> DN 50) | A 1.1 Wedge gate - cast iron (MS) (> DN 50) | A 1.2 Wedge gate - copper alloy (</= DN 50) | A 2.0 Knife gate (RS) | A 3.0 Diaphragm (see also WIMES 8.02) | A 4.0 Pinch | A 5.1 Ball - plastic | A 5.2 Ball - metal | A 6.2 Butterfly - concentric (RS) | A 6.2 Butterfly - concentric (MS) | A 6.3 Butterfly - double eccentric (RS) | A 6.3 Butterfly - double eccentric (MS) | A 6.2 Butterfly - concentric (RS) | B 6.2 Butterfly - concentric (MS) | A 6.3 Butterfly - double eccentric (RS) | A 6.3 Butterfly - double eccentric (MS) | B 1.1 Copper alloy globe (up to DN 100) | B 2.0 Eccentric plug | B 3.0 V-port ball | B 4.0 Piston/plunger/needle | B 5.0 Cone type free discharge | B 6.0 Sumnerged discharge | B 7.0 Needle (up to DN 18) | C 1.0 Line pressure driven control | C 2.0 Direct acting, float act. level control | C 3.0 Direct acting, pressure reducing | D 2.0 Swing disc (RS) | D 2.0 Swing disc (MS) | D 3.0 Resilient hinge disc | D 4.0 Recoil swing disc | D 5.0 Recoil resilient hinge disc | D 6.0 Non-Slam Twin plate (RS) | D 6.0 Non-Slam Twin plate (MS) | D 7.0 Non-Slam Nozzle | D 8.0 Swing or lift (BS 5154) (</= DN 50) | D 9.0 Ball | D 10.0 Duckbill (end of pipe duties) | D 11.0 Foot (maintaining pump prime) | D 12.0 Anti-pollution | E 2.0 Direct, spring operated | E 3.0 Pinch | E 4.0 Pallet type | F 2.0 Single small orifice | F 3.0 Single large orifice | F 4.0 Double orifice | F 5.0 Triple orifice | F 6.0 Vacuum Breaker | G 1.0 Solenoid | G 2.0 Flap (end of pipe duties) | G 3.0 Fire hydrant
PROCESS FLUID
Raw water
Partially treated water (typically < 2 % DS)
Potable water
Unscreened sewage | [30 empty] | 2
Screened sewage
Primary, secondary or final effluent (typ. < 2 % DS) | [8 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [33 empty] | 1
Thin sludges (2 to 8 % DS)
Thick sludges (> 8 % DS)
Dosing chemicals (refer also to WIMES 8.02)
Fuel
Air | [9 empty] | 4 | [23 empty] | 3
Biogas | [33 empty] | 3
LOCATION
Buried
Submerged
Within valve chamber
Above ground level
KEY
COLOURS
Unpreferred choice/unsuitable for use
Refer to Purchaser
Preferred choice/suitable for use
ABBREVIATIONS AND NUMBERS
RS | Resilient seated
MS | Metallic seated
1 | Final effluent only
2 | Multi-door variant unsuitable
3 | When fitted with special springs
4 | Up to the maximum working temperature of the elastomeric seating material
Note on S10: Really?
Note on S18: Are we sure?

## WIMES 8.09 - Appendix K (2)
DUTY |  | ISOLATING | [11 empty] | REGULATING | [10 empty] | CONTROL |  |  | CHECK (NON-RETURN) | [12 empty] | SAFETY |  |  | AIR |  |  |  |  | MISCELL.
VALVE TYPE |  | A 1.1 Wedge gate - cast iron (RS) (> DN 50) | A 1.1 Wedge gate - cast iron (MS) (> DN 50) | A 1.2 Wedge gate - copper alloy (</= DN 50) | A 2.0 Knife gate (RS) | A 3.0 Diaphragm (see also WIMES 8.02) | A 4.0 Pinch | A 5.1 Ball - plastic | A 5.2 Ball - metal | A 6.2 Butterfly - concentric (RS) | A 6.2 Butterfly - concentric (MS) | A 6.3 Butterfly - double eccentric (RS) | A 6.3 Butterfly - double eccentric (MS) | A 6.2 Butterfly - concentric (RS) | B 6.2 Butterfly - concentric (MS) | A 6.3 Butterfly - double eccentric (RS) | A 6.3 Butterfly - double eccentric (MS) | B 1.1 Copper alloy globe (up to DN 100) | B 2.0 Eccentric plug | B 3.0 V-port ball | B 4.0 Piston/plunger/needle | B 5.0 Cone type free discharge | B 6.0 Sumnerged discharge | B 7.0 Needle (up to DN 18) | C 1.0 Line pressure driven control | C 2.0 Direct acting, float act. level control | C 3.0 Direct acting, pressure reducing | D 2.0 Swing disc (RS) | D 2.0 Swing disc (MS) | D 3.0 Resilient hinge disc | D 4.0 Recoil swing disc | D 5.0 Recoil resilient hinge disc | D 6.0 Non-Slam Twin plate (RS) | D 6.0 Non-Slam Twin plate (MS) | D 7.0 Non-Slam Nozzle | D 8.0 Swing or lift (BS 5154) (</= DN 50) | D 9.0 Ball | D 10.0 Duckbill (end of pipe duties) | D 11.0 Foot (maintaining pump prime) | D 12.0 Anti-pollution | E 2.0 Direct, spring operated | E 3.0 Pinch | E 4.0 Pallet type | F 2.0 Single small orifice | F 3.0 Single large orifice | F 4.0 Double orifice | F 5.0 Triple orifice | F 6.0 Vacuum Breaker | G 1.0 Solenoid | G 2.0 Flap (end of pipe duties) | G 3.0 Fire hydrant
PROCESS FLUID
Raw water
Partially treated water (typically < 2 % DS)
Potable water
Unscreened sewage | [30 empty] | 2
Screened sewage
Primary, secondary or final effluent (typ. < 2 % DS) | [8 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [33 empty] | 1
Thin sludges (2 to 8 % DS)
Thick sludges (> 8 % DS)
Dosing chemicals (refer also to WIMES 8.02)
Fuel
Air | [9 empty] | 4 | [23 empty] | 3
Biogas |  | 5 | 5 | [30 empty] | 3
LOCATION
Buried
Submerged
Within valve chamber
Above ground level
KEY
COLOURS
Unpreferred choice/unsuitable for use
Refer to Purchaser
Preferred choice/suitable for use
ABBREVIATIONS AND NUMBERS
RS | Resilient seated
MS | Metallic seated
1 | Final effluent only
2 | Multi-door variant unsuitable
3 | When fitted with special springs
4 | Up to the maximum working temperature of the elastomeric seating material
5 | ECV/AECV duties only
Note on S10: Really?
Note on S18: Are we sure?